## Slide 1
TOPCon N type
Mono-crystalline
630-650Watt full Black
0~+5% POWER TOLERANCE
High efficiency TOPCon N - type solar module
30 years material process warranty
30 years power linear warranty
IEC61215(2016), IEC61730(2016) ISO9001:2015: Quality management system ISO14001:2015: Environmental management system ISO45001:2018: Occupational health and safety management system
Strong Mechancial Strength
Passes the wind load test of 2400Pa and the snow load test of 5400Pa
PID resistance
The attenuation probability of PID phenomenon is minimized through solar cell production technology optimization and raw material control
Multiple busbar and Half cell technique
More light utilization and current collection capabilities, effectively improving product power output and reliability
Lower attenuation
N-type，Components have better reliability and lower LID/LETID attenuation
Harsh environmental adaptation
Third party certification for salt spray and ammonnia corrosion tests
Module characteristics
year
Linear decay of 0.4% per year over 30 years
Long and reliable quality assurance
Power output
16/18BB

## Slide 2
Electrical Parameters |  |  |  |  |  |  |  |  |  | 
Model Type | ESM-630T |  | ESM-635T |  | ESM-640T |  | ESM-645T |  | ESM-650T | 
 | STC | NOCT | STC | NOCT | STC | NOCT | STC | NOCT | STC | NOCT
Maximum Power（Pmax） | 630 | 473 | 635 | 477 | 640 | 481 | 645 | 485 | 650 | 489
Open Circuit Voltage（Voc） | 55.93 | 53.12 | 56.08 | 53.27 | 56.23 | 53.42 | 56.38 | 53.57 | 56.53 | 53.72
Short Circuit Current（Isc） | 14.37 | 11.60 | 14.44 | 11.67 | 14.51 | 11.74 | 14.58 | 11.81 | 14.65 | 11.89
MaximumPowerVoltage（Vmp） | 46.06 | 42.83 | 46.18 | 42.95 | 46.28 | 43.05 | 46.38 | 43.15 | 46.48 | 43.25
MaximumPowerCurrent（Imp） | 13.67 | 11.04 | 13.75 | 11.10 | 13.83 | 11.17 | 13.91 | 11.24 | 13.98 | 11.31
ModuleEfficiency - ηm（%） | 22.53 |  | 22.71 |  | 22.89 |  | 23.07 |  | 23.25 | 
Operational Temperature |  | -40℃~+85℃ |  |  |  |  |  |  |  | 
Maximum System Voltage |  | 1500VDC |  |  |  |  |  |  |  | 
Maximum Series Fuse Rating |  | 25A |  |  |  |  |  |  |  | 
Power Tolerance |  | 0~+5W |  |  |  |  |  |  |  | 
Temperature Coefficient of Pmax |  | -0.360%/℃ |  |  |  |  |  |  |  | 
Temperature Coefficient of Voc |  | -0.260%/℃ |  |  |  |  |  |  |  | 
Temperature Coefficient of Isc |  | +0.04%/℃ |  |  |  |  |  |  |  | 
Nominal Operating Cell Temperature |  | 45±2℃ |  |  |  |  |  |  |  | 
Safety Class |  | Class II |  |  |  |  |  |  |  | 
Max Load（Front/back） |  | 5400Pa/2400Pa |  |  |  |  |  |  |  | 
STC: Irradiance 1000W/㎡ Cell temperature 25℃ Atmospheric quality =1.5
NOCT:Irradiance 800W/㎡ Ambient temperature 20℃ Atmospheric quality =1.5 Wind speed 1m/S
Mechanical Diagrams
Curve
Cell type | N type mono crystalline 182mm
Half-cell quantity | 156pcs（26×6）
Dimension | 2465×1134×30mm
Weight | 31kg±3%
Glass | 3.2mm
Frame | Black Anodized Aluminum Alloy
Junction Box | IP68
Cable | 400mm（can be customized）
Packing Details:
36pcs/pallet
40GP:16 pallets/HQ, 572pcs/40'HQ
Specification
EINNOVA SOLARLINE ENERGY CORP. LIMITED
210000 Nanjing
PEOPLE‘S REPUBLIC OF CHINA
TEL：+86-25-8479-2033
Cell: +86-138-13088384
EMAIL : emma.wu@einnova-solarline.com
Website：www.einnova-solarline.com
Front
Back
Side
The company reserves the right of final right of adjustment of this file.